## Sheet1
featureType | code | identifier | name | nameEn | description | applicableScope | sortOrder | specJson
EVENT | E-GEN-0001 | deviceOnline | 设备上线 | Device Online | 设备连接上线 | 通用 | 1 | {"level":"INFO","outputParams":[{"dataType":"DATE","key":"timestamp"}]}
SERVICE | S-GEN-0001 | turnOn | 开机 | Turn On | 设备开机 | 通用 | 1 | {"callMode":"ASYNC","outputParams":[{"dataType":"BOOL","key":"success"}]}
EVENT | E-GEN-0002 | deviceOffline | 设备离线 | Device Offline | 设备断开连接 | 通用 | 2 | {"level":"INFO","outputParams":[{"dataType":"DATE","key":"timestamp"},{"dataType":"DOUBLE","key":"offlineDuration","unit":{"unitCode":"second","unitSymbol":"s"}}]}
SERVICE | S-GEN-0002 | turnOff | 关机 | Turn Off | 设备关机 | 通用 | 2 | {"callMode":"ASYNC","outputParams":[{"dataType":"BOOL","key":"success"}]}
EVENT | E-GEN-0003 | runStatusChanged | 运行状态变更 | Run Status Changed | 运行状态切换 | 通用 | 3 | {"level":"INFO","outputParams":[{"dataType":"ENUM","key":"oldStatus"},{"dataType":"ENUM","key":"newStatus"}]}
SERVICE | S-GEN-0003 | restart | 重启 | Restart | 延时重启设备 | 通用 | 3 | {"callMode":"ASYNC","inputParams":[{"constraints":{"max":3600,"min":0},"dataType":"DOUBLE","key":"delay","unit":{"unitCode":"second","unitSymbol":"s"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
EVENT | E-GEN-0004 | parameterOverLimit | 参数越限告警 | Parameter Over Limit | 测量参数超出设定阈值 | 通用 | 4 | {"level":"ALERT","outputParams":[{"dataType":"TEXT","key":"parameterName"},{"dataType":"DOUBLE","key":"currentValue"},{"dataType":"DOUBLE","key":"limitValue"},{"dataType":"TEXT","key":"unit"}]}
SERVICE | S-GEN-0004 | setRunMode | 设置运行模式 | Set Run Mode | 切换运行模式 | 通用 | 4 | {"callMode":"ASYNC","inputParams":[{"dataType":"ENUM","key":"runMode"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
EVENT | E-GEN-0005 | communicationError | 通信异常告警 | Communication Error | 通信链路异常 | 通用 | 5 | {"level":"ALERT","outputParams":[{"dataType":"ENUM","key":"errorType"},{"dataType":"TEXT","key":"detail"}]}
SERVICE | S-GEN-0005 | faultReset | 故障复位 | Fault Reset | 清除故障状态 | 通用 | 5 | {"callMode":"ASYNC","outputParams":[{"dataType":"BOOL","key":"success"}]}
EVENT | E-GEN-0006 | deviceFault | 设备故障 | Device Fault | 设备发生故障 | 通用 | 6 | {"level":"ERROR","outputParams":[{"dataType":"INT","key":"faultCode"},{"dataType":"TEXT","key":"faultDesc"},{"dataType":"DATE","key":"faultTime"}]}
SERVICE | S-GEN-0006 | getProperty | 读取属性 | Get Property | 同步读取指定属性当前值 | 通用 | 6 | {"callMode":"SYNC","inputParams":[{"dataType":"TEXT","key":"propertyIdentifier"}],"outputParams":[{"dataType":"STRUCT","key":"propertyValue"}]}
EVENT | E-GEN-0007 | faultRecovery | 故障恢复 | Fault Recovery | 故障已恢复 | 通用 | 7 | {"level":"INFO","outputParams":[{"dataType":"INT","key":"faultCode"},{"dataType":"DOUBLE","key":"faultDuration","unit":{"unitCode":"minute","unitSymbol":"min"}}]}
SERVICE | S-GEN-0007 | setProperty | 设置属性 | Set Property | 设置指定属性值 | 通用 | 7 | {"callMode":"ASYNC","inputParams":[{"dataType":"TEXT","key":"propertyIdentifier"},{"dataType":"STRUCT","key":"propertyValue"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
EVENT | E-GEN-0008 | maintenanceReminder | 维保提醒 | Maintenance Reminder | 设备需要维护保养 | 通用 | 8 | {"level":"INFO","outputParams":[{"dataType":"ENUM","key":"maintenanceType"},{"dataType":"DOUBLE","key":"remainingTime","unit":{"unitCode":"hour","unitSymbol":"h"}}]}
SERVICE | S-GEN-0008 | queryHistory | 查询历史数据 | Query History | 查询指定时间段历史数据 | 通用 | 8 | {"callMode":"SYNC","inputParams":[{"dataType":"DATE","key":"startTime"},{"dataType":"DATE","key":"endTime"},{"dataType":"ARRAY","key":"propertyIdentifiers"}],"outputParams":[{"dataType":"ARRAY","key":"historyData"}]}
PROPERTY | P-RUN-0001 | powerSwitch | 开关状态 | Power Switch | 设备开关 | 通用 | 101 | {"accessMode":"RW","boolLabels":{"false":"关","true":"开"},"category":"runtime","dataType":"BOOL"}
PROPERTY | P-RUN-0002 | runMode | 运行模式 | Run Mode | 运行模式选择 | 通用 | 102 | {"accessMode":"RW","category":"runtime","dataType":"ENUM","enumItems":[{"label":"停机","value":0},{"label":"手动","value":1},{"label":"自动","value":2},{"label":"远程","value":3}]}
PROPERTY | P-RUN-0003 | runStatus | 运行状态 | Run Status | 设备当前运行状态 | 通用 | 103 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"停止","value":0},{"label":"运行","value":1},{"label":"待机","value":2},{"label":"故障","value":3}]}
PROPERTY | P-RUN-0004 | faultCode | 故障代码 | Fault Code | 0=无故障，其他=故障代码 | 通用 | 104 | {"accessMode":"R","category":"runtime","dataType":"INT"}
PROPERTY | P-RUN-0005 | faultDesc | 故障描述 | Fault Description | 故障文本描述 | 通用 | 105 | {"accessMode":"R","category":"runtime","dataType":"TEXT","textMaxLength":256}
PROPERTY | P-RUN-0006 | localRemote | 本地/远程 | Local/Remote | 控制权位置 | 通用 | 106 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"本地","value":0},{"label":"远程","value":1}]}
PROPERTY | P-RUN-0007 | autoManual | 手自动 | Auto/Manual | 手/自动模式 | 通用 | 107 | {"accessMode":"RW","category":"runtime","dataType":"ENUM","enumItems":[{"label":"手动","value":0},{"label":"自动","value":1}]}
PROPERTY | P-RAT-0001 | model | 设备型号 | Model | 出厂型号 | 通用 | 201 | {"accessMode":"R","category":"rated","dataType":"TEXT","isRated":true,"textMaxLength":128}
PROPERTY | P-RAT-0002 | manufacturer | 制造商 | Manufacturer | 设备生产厂家 | 通用 | 202 | {"accessMode":"R","category":"rated","dataType":"TEXT","isRated":true,"textMaxLength":128}
PROPERTY | P-RAT-0003 | manufactureDate | 出厂日期 | Manufacture Date | 出厂日期 | 通用 | 203 | {"accessMode":"R","category":"rated","dataType":"DATE","isRated":true}
PROPERTY | P-RAT-0004 | serialNumber | 序列号 | Serial Number | 出厂序列号 | 通用 | 204 | {"accessMode":"R","category":"rated","dataType":"TEXT","isRated":true,"textMaxLength":64}
PROPERTY | P-RAT-0005 | ratedVoltage | 额定电压 | Rated Voltage | 额定电压 | 通用 | 205 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"volt","unitSymbol":"V"}}
PROPERTY | P-RAT-0006 | ratedCurrent | 额定电流 | Rated Current | 额定电流 | 通用 | 206 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"ampere","unitSymbol":"A"}}
PROPERTY | P-RAT-0007 | ratedPower | 额定功率 | Rated Power | 额定功率 | 通用 | 207 | {"accessMode":"R","category":"rated","constraints":{"max":100000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | P-RAT-0008 | ratedFrequency | 额定频率 | Rated Frequency | 额定频率 | 通用 | 208 | {"accessMode":"R","category":"rated","constraints":{"max":100,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"hertz","unitSymbol":"Hz"}}
PROPERTY | P-RAT-0009 | ipRating | 防护等级 | IP Rating | 如 IP42/IP54 | 通用 | 209 | {"accessMode":"R","category":"rated","dataType":"TEXT","isRated":true,"textMaxLength":16}
PROPERTY | P-RAT-0010 | insulationClass | 绝缘等级 | Insulation Class | 绝缘耐热等级 | 通用 | 210 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"A级","value":0},{"label":"E级","value":1},{"label":"B级","value":2},{"label":"F级","value":3},{"label":"H级","value":4},{"label":"C级","value":5}],"isRated":true}
PROPERTY | P-STA-0001 | totalRunTime | 累计运行时间 | Total Run Time | 累计运行小时数 | 通用 | 301 | {"accessMode":"R","category":"statistic","dataType":"DOUBLE","unit":{"unitCode":"hour","unitSymbol":"h"}}
PROPERTY | P-STA-0002 | totalEnergy | 累计能耗 | Total Energy | 累计耗电量 | 通用 | 302 | {"accessMode":"R","category":"statistic","dataType":"DOUBLE","unit":{"unitCode":"kilowatt_hour","unitSymbol":"kWh"}}
PROPERTY | P-STA-0003 | startCount | 启动次数 | Start Count | 累计启动次数 | 通用 | 303 | {"accessMode":"R","category":"statistic","dataType":"INT"}
PROPERTY | P-STA-0004 | faultCount | 故障次数 | Fault Count | 累计故障次数 | 通用 | 304 | {"accessMode":"R","category":"statistic","dataType":"INT"}
PROPERTY | P-STA-0005 | todayRunTime | 今日运行时间 | Today Run Time | 当日累计运行小时 | 通用 | 305 | {"accessMode":"R","category":"statistic","constraints":{"max":24,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"hour","unitSymbol":"h"}}
PROPERTY | P-STA-0006 | todayEnergy | 今日能耗 | Today Energy | 当日累计能耗 | 通用 | 306 | {"accessMode":"R","category":"statistic","dataType":"DOUBLE","unit":{"unitCode":"kilowatt_hour","unitSymbol":"kWh"}}
PROPERTY | P-ENV-0001 | ambientTemp | 环境温度 | Ambient Temp | 设备环境温度 | 通用 | 401 | {"accessMode":"R","category":"environment","constraints":{"max":80,"min":-40},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-ENV-0002 | ambientHumidity | 环境湿度 | Ambient Humidity | 设备环境湿度 | 通用 | 402 | {"accessMode":"R","category":"environment","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent_rh","unitSymbol":"%RH"}}
PROPERTY | P-HVAC-0001 | supplyWaterTemp | 供水温度 | Supply Water Temp | 供水温度 | 冷机/锅炉/换热器 | 6001 | {"accessMode":"R","category":"measurement","constraints":{"max":200,"min":-40},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0002 | returnWaterTemp | 回水温度 | Return Water Temp | 回水温度 | 冷机/锅炉/换热器 | 6002 | {"accessMode":"R","category":"measurement","constraints":{"max":200,"min":-40},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0003 | supplyWaterPressure | 供水压力 | Supply Water Pressure | 供水压力 | 冷机/水泵 | 6003 | {"accessMode":"R","category":"measurement","constraints":{"max":10,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}
PROPERTY | P-HVAC-0004 | returnWaterPressure | 回水压力 | Return Water Pressure | 回水压力 | 冷机/水泵 | 6004 | {"accessMode":"R","category":"measurement","constraints":{"max":10,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}
PROPERTY | P-HVAC-0005 | waterFlowRate | 水流量 | Water Flow Rate | 水流量 | 冷机/水泵 | 6005 | {"accessMode":"R","category":"measurement","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | P-HVAC-0006 | operationMode | 供冷/供热模式 | Operation Mode | 运行模式 | 冷机/热泵/空调末端 | 6006 | {"accessMode":"RW","category":"setting","dataType":"ENUM","enumItems":[{"label":"制冷","value":0},{"label":"制热","value":1},{"label":"通风","value":2},{"label":"除湿","value":3},{"label":"自动","value":4}]}
PROPERTY | P-HVAC-0007 | setTemperature | 设定温度 | Set Temperature | 设定温度 | 空调末端/新风机组 | 6007 | {"accessMode":"RW","category":"setting","constraints":{"max":60,"min":-20},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0008 | supplyAirTemp | 送风温度 | Supply Air Temp | 送风温度 | 空调末端/新风机组 | 6008 | {"accessMode":"R","category":"measurement","constraints":{"max":80,"min":-40},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0009 | returnAirTemp | 回风温度 | Return Air Temp | 回风温度 | 空调末端 | 6009 | {"accessMode":"R","category":"measurement","constraints":{"max":80,"min":-40},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0010 | supplyAirHumidity | 送风湿度 | Supply Air Humidity | 送风湿度 | 空调末端/新风机组 | 6010 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent_rh","unitSymbol":"%RH"}}
PROPERTY | P-HVAC-0011 | damperPosition | 风阀开度 | Damper Position | 风阀开度 | 通风机/空调末端 | 6011 | {"accessMode":"RW","category":"setting","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-HVAC-0012 | valvePosition | 水阀开度 | Valve Position | 水阀开度 | 空调末端/换热器 | 6012 | {"accessMode":"RW","category":"setting","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-HVAC-0013 | fanFrequency | 风机频率 | Fan Frequency | 变频风机频率 | 通风机/空调末端 | 6013 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"hertz","unitSymbol":"Hz"}}
PROPERTY | P-HVAC-0014 | fanSpeed | 风机转速 | Fan Speed | 风机转速 | 通风机 | 6014 | {"accessMode":"R","category":"measurement","constraints":{"max":30000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"rpm","unitSymbol":"rpm"}}
PROPERTY | P-HVAC-0015 | filterPressureDiff | 过滤器压差 | Filter Pressure Diff | 过滤器压差 | 通风机/新风机组 | 6015 | {"accessMode":"R","category":"measurement","constraints":{"max":2000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"pascal","unitSymbol":"Pa"}}
PROPERTY | P-HVAC-0016 | compressorStatus | 压缩机运行状态 | Compressor Status | 压缩机状态 | 制冷机组 | 6016 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"停止","value":0},{"label":"运行","value":1},{"label":"卸载","value":2},{"label":"故障","value":3}]}
PROPERTY | P-HVAC-0017 | compressorLoadRate | 压缩机负载率 | Compressor Load Rate | 压缩机负载率 | 制冷机组 | 6017 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-HVAC-0018 | evaporatingTemp | 蒸发温度 | Evaporating Temp | 蒸发温度 | 制冷机组 | 6018 | {"accessMode":"R","category":"measurement","constraints":{"max":30,"min":-50},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0019 | condensingTemp | 冷凝温度 | Condensing Temp | 冷凝温度 | 制冷机组 | 6019 | {"accessMode":"R","category":"measurement","constraints":{"max":80,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0020 | condenserInletTemp | 冷却水进水温度 | Condenser Inlet Temp | 冷却水进水温度 | 制冷机组/冷却塔 | 6020 | {"accessMode":"R","category":"measurement","constraints":{"max":60,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0021 | condenserOutletTemp | 冷却水出水温度 | Condenser Outlet Temp | 冷却水出水温度 | 制冷机组/冷却塔 | 6021 | {"accessMode":"R","category":"measurement","constraints":{"max":50,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0022 | currentCoolingCapacity | 实时制冷量 | Current Cooling Capacity | 实时制冷量 | 制冷机组 | 6022 | {"accessMode":"R","category":"measurement","constraints":{"max":50000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | P-HVAC-0023 | currentCOP | 实时COP | Current COP | 实时能效 | 制冷机组 | 6023 | {"accessMode":"R","category":"measurement","constraints":{"max":15,"min":0},"dataType":"DOUBLE"}
PROPERTY | P-HVAC-0024 | currentPower | 实时功率 | Current Power | 实时功率 | 通用 | 6024 | {"accessMode":"R","category":"measurement","constraints":{"max":100000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | P-HVAC-0025 | freshAirTemp | 新风温度 | Fresh Air Temp | 新风温度 | 新风机组 | 6025 | {"accessMode":"R","category":"measurement","constraints":{"max":60,"min":-40},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-HVAC-0026 | freshAirHumidity | 新风湿度 | Fresh Air Humidity | 新风湿度 | 新风机组 | 6026 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent_rh","unitSymbol":"%RH"}}
PROPERTY | P-HVAC-0027 | co2Concentration | CO2浓度 | CO2 Concentration | 二氧化碳浓度 | 新风机组/空调末端 | 6027 | {"accessMode":"R","category":"measurement","constraints":{"max":5000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"ppm","unitSymbol":"ppm"}}
PROPERTY | P-HVAC-0028 | setFanSpeed | 设定风速 | Set Fan Speed | 设定风速档位 | 空调末端 | 6028 | {"accessMode":"RW","category":"setting","dataType":"ENUM","enumItems":[{"label":"低速","value":0},{"label":"中速","value":1},{"label":"高速","value":2},{"label":"自动","value":3}]}
PROPERTY | P-WP-0001 | waterLevel | 水箱液位 | Water Level | 水箱液位 | 水箱/水池 | 6201 | {"accessMode":"R","category":"measurement","constraints":{"max":20,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"meter","unitSymbol":"m"}}
PROPERTY | P-WP-0002 | waterLevelPercent | 液位百分比 | Water Level Percent | 液位百分比 | 水箱/水池 | 6202 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-WP-0003 | pipePressure | 管道压力 | Pipe Pressure | 管道压力 | 水泵/管网 | 6203 | {"accessMode":"R","category":"measurement","constraints":{"max":10,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}
PROPERTY | P-WP-0004 | instantFlowRate | 瞬时流量 | Instant Flow Rate | 瞬时流量 | 水泵 | 6204 | {"accessMode":"R","category":"measurement","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | P-WP-0005 | totalFlowVolume | 累计流量 | Total Flow Volume | 累计流量 | 水泵 | 6205 | {"accessMode":"R","category":"statistic","dataType":"DOUBLE","unit":{"unitCode":"cubic_meter","unitSymbol":"m³"}}
PROPERTY | P-WP-0006 | pumpFrequency | 水泵频率 | Pump Frequency | 变频水泵频率 | 变频水泵 | 6206 | {"accessMode":"RW","category":"setting","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"hertz","unitSymbol":"Hz"}}
PROPERTY | P-WP-0007 | pumpSpeed | 水泵转速 | Pump Speed | 水泵转速 | 水泵 | 6207 | {"accessMode":"R","category":"measurement","constraints":{"max":30000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"rpm","unitSymbol":"rpm"}}
PROPERTY | P-WP-0008 | outletWaterTemp | 出水温度 | Outlet Water Temp | 热水出水温度 | 热水设备 | 6208 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-WP-0009 | setWaterTemp | 设定水温 | Set Water Temp | 设定热水温度 | 热水设备 | 6209 | {"accessMode":"RW","category":"setting","constraints":{"max":80,"min":20},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-WP-0010 | chlorineConcentration | 余氯浓度 | Chlorine Concentration | 余氯浓度 | 水处理设备 | 6210 | {"accessMode":"R","category":"measurement","constraints":{"max":10,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"mg_per_l","unitSymbol":"mg/L"}}
PROPERTY | P-WP-0011 | turbidity | 浊度 | Turbidity | 浊度 | 水处理设备 | 6211 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"ntu","unitSymbol":"NTU"}}
PROPERTY | P-WP-0012 | phValue | pH值 | pH Value | 酸碱度 | 水处理设备 | 6212 | {"accessMode":"R","category":"measurement","constraints":{"max":14,"min":0},"dataType":"DOUBLE"}
PROPERTY | P-EL-0001 | voltage | 电压 | Voltage | 工作电压 | 变压器/配电柜 | 6301 | {"accessMode":"R","category":"measurement","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"volt","unitSymbol":"V"}}
PROPERTY | P-EL-0002 | current | 电流 | Current | 工作电流 | 变压器/配电柜 | 6302 | {"accessMode":"R","category":"measurement","constraints":{"max":100000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"ampere","unitSymbol":"A"}}
PROPERTY | P-EL-0003 | activePower | 有功功率 | Active Power | 有功功率 | 变压器/配电柜 | 6303 | {"accessMode":"R","category":"measurement","constraints":{"max":100000,"min":-100000},"dataType":"DOUBLE","unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | P-EL-0004 | reactivePower | 无功功率 | Reactive Power | 无功功率 | 变压器/配电柜 | 6304 | {"accessMode":"R","category":"measurement","constraints":{"max":100000,"min":-100000},"dataType":"DOUBLE","unit":{"unitCode":"kilovar","unitSymbol":"kvar"}}
PROPERTY | P-EL-0005 | powerFactor | 功率因数 | Power Factor | 功率因数 | 变压器/配电柜 | 6305 | {"accessMode":"R","category":"measurement","constraints":{"max":1,"min":-1},"dataType":"DOUBLE"}
PROPERTY | P-EL-0006 | frequency | 频率 | Frequency | 工作频率 | 变压器/发电机组 | 6306 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"hertz","unitSymbol":"Hz"}}
PROPERTY | P-EL-0007 | activeEnergy | 有功电能 | Active Energy | 有功电能 | 电表 | 6307 | {"accessMode":"R","category":"statistic","dataType":"DOUBLE","unit":{"unitCode":"kilowatt_hour","unitSymbol":"kWh"}}
PROPERTY | P-EL-0008 | reactiveEnergy | 无功电能 | Reactive Energy | 无功电能 | 电表 | 6308 | {"accessMode":"R","category":"statistic","dataType":"DOUBLE","unit":{"unitCode":"kvarh","unitSymbol":"kvarh"}}
PROPERTY | P-EL-0009 | transformerTemp | 变压器温度 | Transformer Temp | 变压器温度 | 变压器 | 6309 | {"accessMode":"R","category":"measurement","constraints":{"max":200,"min":-40},"dataType":"DOUBLE","unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | P-EL-0010 | loadRate | 负载率 | Load Rate | 负载率 | 变压器 | 6310 | {"accessMode":"R","category":"measurement","constraints":{"max":150,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-EL-0011 | batteryVoltage | 电池电压 | Battery Voltage | 电池电压 | UPS/EPS | 6311 | {"accessMode":"R","category":"measurement","constraints":{"max":1000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"volt","unitSymbol":"V"}}
PROPERTY | P-EL-0012 | batteryRemaining | 电池剩余容量 | Battery Remaining | 电池剩余容量 | UPS/EPS | 6312 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-EL-0013 | remainingBackupTime | 剩余后备时间 | Remaining Backup Time | 剩余后备时间 | UPS/EPS | 6313 | {"accessMode":"R","category":"measurement","constraints":{"max":1440,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"minute","unitSymbol":"min"}}
PROPERTY | P-EL-0014 | mainsStatus | 市电状态 | Mains Status | 市电状态 | UPS/EPS/发电机组 | 6314 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"正常","value":0},{"label":"异常","value":1},{"label":"中断","value":2}]}
PROPERTY | P-EL-0015 | switchStatus | 开关状态 | Switch Status | 断路器开关状态 | 配电柜/箱 | 6315 | {"accessMode":"R","boolLabels":{"false":"分闸","true":"合闸"},"category":"runtime","dataType":"BOOL"}
PROPERTY | P-EL-0016 | illuminance | 照度 | Illuminance | 照度 | 照明设备 | 6316 | {"accessMode":"R","category":"measurement","constraints":{"max":100000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"lux","unitSymbol":"Lux"}}
PROPERTY | P-EL-0017 | dimmingLevel | 调光级别 | Dimming Level | 调光级别 | 照明设备 | 6317 | {"accessMode":"RW","category":"setting","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-FP-0001 | firePipePressure | 管网压力 | Pipe Pressure | 消防管网压力 | 消防水泵/消火栓 | 6401 | {"accessMode":"R","category":"measurement","constraints":{"max":5,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}
PROPERTY | P-FP-0002 | fireWaterLevel | 消防水池液位 | Fire Water Level | 消防水池液位 | 消防水箱 | 6402 | {"accessMode":"R","category":"measurement","constraints":{"max":10,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"meter","unitSymbol":"m"}}
PROPERTY | P-FP-0003 | alarmStatus | 报警状态 | Alarm Status | 火警状态 | 火灾报警系统 | 6403 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"正常","value":0},{"label":"火警","value":1},{"label":"预警","value":2},{"label":"故障","value":3}]}
PROPERTY | P-FP-0004 | alarmZone | 报警区域 | Alarm Zone | 报警区域 | 火灾报警系统 | 6404 | {"accessMode":"R","category":"runtime","dataType":"TEXT","textMaxLength":128}
PROPERTY | P-FP-0005 | sprinklerStatus | 喷头状态 | Sprinkler Status | 喷头状态 | 自动喷水系统 | 6405 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"正常","value":0},{"label":"动作","value":1},{"label":"故障","value":2}]}
PROPERTY | P-FP-0006 | smokeValveStatus | 排烟阀状态 | Smoke Valve Status | 排烟阀状态 | 防排烟系统 | 6406 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"关闭","value":0},{"label":"开启","value":1},{"label":"故障","value":2}]}
PROPERTY | P-FP-0007 | fireDoorStatus | 防火门状态 | Fire Door Status | 防火门状态 | 防火门 | 6407 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"关闭","value":0},{"label":"开启","value":1},{"label":"故障","value":2}]}
PROPERTY | P-FP-0008 | fireShutterPosition | 防火卷帘位置 | Fire Shutter Position | 防火卷帘位置 | 防火卷帘 | 6408 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-FP-0009 | gasSuppressionStatus | 气体灭火状态 | Gas Suppression Status | 气体灭火状态 | 气体灭火系统 | 6409 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"正常","value":0},{"label":"喷放","value":1},{"label":"故障","value":2}]}
PROPERTY | P-FP-0010 | selfTestStatus | 系统自检状态 | Self Test Status | 系统自检状态 | 火灾报警系统 | 6410 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"正常","value":0},{"label":"自检中","value":1},{"label":"自检异常","value":2}]}
PROPERTY | P-ELV-0001 | currentFloor | 当前楼层 | Current Floor | 电梯当前楼层 | 电梯 | 6501 | {"accessMode":"R","category":"measurement","constraints":{"max":200,"min":-10},"dataType":"INT"}
PROPERTY | P-ELV-0002 | travelDirection | 运行方向 | Travel Direction | 电梯运行方向 | 电梯 | 6502 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"停止","value":0},{"label":"上行","value":1},{"label":"下行","value":2}]}
PROPERTY | P-ELV-0003 | carPassengerCount | 轿厢内人数 | Car Passenger Count | 轿厢内人数 | 电梯 | 6503 | {"accessMode":"R","category":"measurement","constraints":{"max":50,"min":0},"dataType":"INT"}
PROPERTY | P-ELV-0004 | currentLoad | 当前载重 | Current Load | 当前载重 | 电梯 | 6504 | {"accessMode":"R","category":"measurement","constraints":{"max":20000,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"kilogram","unitSymbol":"kg"}}
PROPERTY | P-ELV-0005 | loadPercentage | 载重百分比 | Load Percentage | 载重百分比 | 电梯 | 6505 | {"accessMode":"R","category":"measurement","constraints":{"max":110,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-ELV-0006 | doorStatus | 门状态 | Door Status | 门状态 | 电梯 | 6506 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"关门","value":0},{"label":"开门","value":1},{"label":"开门中","value":2},{"label":"关门中","value":3}]}
PROPERTY | P-ELV-0007 | currentSpeed | 运行速度 | Current Speed | 运行速度 | 电梯 | 6507 | {"accessMode":"R","category":"measurement","constraints":{"max":20,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"meter_per_second","unitSymbol":"m/s"}}
PROPERTY | P-ELV-0008 | lockStatus | 锁梯状态 | Lock Status | 锁梯状态 | 电梯 | 6508 | {"accessMode":"RW","boolLabels":{"false":"解锁","true":"锁梯"},"category":"setting","dataType":"BOOL"}
PROPERTY | P-ELV-0009 | fireReturnStatus | 消防返回状态 | Fire Return Status | 消防返回状态 | 电梯 | 6509 | {"accessMode":"R","boolLabels":{"false":"正常","true":"消防返回"},"category":"runtime","dataType":"BOOL"}
PROPERTY | P-ELV-0010 | escalatorDirection | 扶梯运行方向 | Escalator Direction | 扶梯运行方向 | 自动扶梯 | 6510 | {"accessMode":"RW","category":"setting","dataType":"ENUM","enumItems":[{"label":"停止","value":0},{"label":"上行","value":1},{"label":"下行","value":2}]}
PROPERTY | P-SM-0001 | onlineStatus | 在线状态 | Online Status | 在线状态 | 摄像机/门禁/传感器 | 6601 | {"accessMode":"R","boolLabels":{"false":"离线","true":"在线"},"category":"runtime","dataType":"BOOL"}
PROPERTY | P-SM-0002 | signalStrength | 信号强度 | Signal Strength | 信号强度 | 无线设备 | 6602 | {"accessMode":"R","category":"measurement","constraints":{"max":0,"min":-120},"dataType":"INT","unit":{"unitCode":"dbm","unitSymbol":"dBm"}}
PROPERTY | P-SM-0003 | cpuUsage | CPU使用率 | CPU Usage | CPU使用率 | 控制器/服务器 | 6603 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-SM-0004 | memoryUsage | 内存使用率 | Memory Usage | 内存使用率 | 控制器/服务器 | 6604 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-SM-0005 | storageUsage | 存储使用率 | Storage Usage | 存储使用率 | NVR/服务器 | 6605 | {"accessMode":"R","category":"measurement","constraints":{"max":100,"min":0},"dataType":"DOUBLE","unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | P-SM-0006 | smDoorStatus | 门状态 | Door Status | 门禁门状态 | 门禁 | 6606 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"关闭","value":0},{"label":"开启","value":1},{"label":"未关","value":2},{"label":"超时未关","value":3}]}
PROPERTY | P-SM-0007 | armStatus | 布防状态 | Arm Status | 入侵报警布防状态 | 入侵报警 | 6607 | {"accessMode":"RW","category":"setting","dataType":"ENUM","enumItems":[{"label":"撤防","value":0},{"label":"外出布防","value":1},{"label":"留守布防","value":2}]}
PROPERTY | P-SM-0008 | measuredValue | 测量值 | Measured Value | 传感器测量值 | 传感器 | 6608 | {"accessMode":"R","category":"measurement","dataType":"DOUBLE"}
PROPERTY | P-SM-0009 | controlOutput | 控制输出值 | Control Output | 控制器输出 | 控制器 | 6609 | {"accessMode":"RW","category":"setting","constraints":{"max":100,"min":0},"dataType":"DOUBLE"}
PROPERTY | P-SM-0010 | networkStatus | 网络连接状态 | Network Status | 网络状态 | 通信设备 | 6610 | {"accessMode":"R","category":"runtime","dataType":"ENUM","enumItems":[{"label":"断开","value":0},{"label":"已连接","value":1},{"label":"连接中","value":2}]}
EVENT | E-HVAC-0001 | supplyTempHigh | 供水温度超高 | Supply Temp High | 供水温度超过设定上限 | 冷机/锅炉 | 7101 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"supplyTemp","unit":{"unitCode":"celsius","unitSymbol":"℃"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"celsius","unitSymbol":"℃"}}]}
EVENT | E-HVAC-0002 | supplyTempLow | 供水温度超低 | Supply Temp Low | 供水温度低于设定下限 | 冷机/锅炉 | 7102 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"supplyTemp","unit":{"unitCode":"celsius","unitSymbol":"℃"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"celsius","unitSymbol":"℃"}}]}
EVENT | E-HVAC-0003 | compressorHighPressure | 压缩机高压保护 | Compressor High Pressure | 压缩机排气压力过高 | 制冷机组 | 7103 | {"level":"ERROR","outputParams":[{"dataType":"DOUBLE","key":"pressure","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}]}
EVENT | E-HVAC-0004 | compressorLowPressure | 压缩机低压保护 | Compressor Low Pressure | 压缩机吸气压力过低 | 制冷机组 | 7104 | {"level":"ERROR","outputParams":[{"dataType":"DOUBLE","key":"pressure","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}]}
EVENT | E-HVAC-0005 | freezeProtection | 防冻保护 | Freeze Protection | 水温接近冰点 | 制冷机组/空调末端 | 7105 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"waterTemp","unit":{"unitCode":"celsius","unitSymbol":"℃"}}]}
EVENT | E-HVAC-0006 | filterClogged | 过滤器堵塞 | Filter Clogged | 过滤器压差过大 | 通风机/新风机组 | 7106 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"pressureDiff","unit":{"unitCode":"pascal","unitSymbol":"Pa"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"pascal","unitSymbol":"Pa"}}]}
EVENT | E-HVAC-0007 | waterFlowSwitchOff | 水流开关断开 | Water Flow Switch Off | 水流中断保护 | 制冷机组/空调末端 | 7107 | {"level":"ERROR","outputParams":null}
EVENT | E-HVAC-0008 | coolingTowerFanFault | 冷却塔风机故障 | Cooling Tower Fan Fault | 冷却塔风机异常 | 冷却塔 | 7108 | {"level":"ERROR","outputParams":[{"dataType":"INT","key":"fanIndex"},{"dataType":"TEXT","key":"faultDesc"}]}
EVENT | E-WP-0001 | highWaterLevel | 高液位告警 | High Water Level | 液位超过高限 | 水箱/水池 | 7201 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"waterLevel","unit":{"unitCode":"meter","unitSymbol":"m"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"meter","unitSymbol":"m"}}]}
EVENT | E-WP-0002 | lowWaterLevel | 低液位告警 | Low Water Level | 液位低于低限 | 水箱/水池 | 7202 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"waterLevel","unit":{"unitCode":"meter","unitSymbol":"m"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"meter","unitSymbol":"m"}}]}
EVENT | E-WP-0003 | overflowAlarm | 溢流告警 | Overflow Alarm | 液位溢流 | 水箱/水池 | 7203 | {"level":"ERROR","outputParams":[{"dataType":"DOUBLE","key":"waterLevel","unit":{"unitCode":"meter","unitSymbol":"m"}}]}
EVENT | E-WP-0004 | pipeOverPressure | 管网超压 | Pipe Over Pressure | 管道压力超高 | 水泵/管网 | 7204 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"pressure","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}]}
EVENT | E-WP-0005 | pipePressureLoss | 管网失压 | Pipe Pressure Loss | 管道压力过低 | 水泵/管网 | 7205 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"pressure","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}]}
EVENT | E-WP-0006 | pumpOverload | 水泵过载 | Pump Overload | 电机过载保护 | 水泵 | 7206 | {"level":"ERROR","outputParams":[{"dataType":"DOUBLE","key":"current","unit":{"unitCode":"ampere","unitSymbol":"A"}},{"dataType":"DOUBLE","key":"ratedCurrent","unit":{"unitCode":"ampere","unitSymbol":"A"}}]}
EVENT | E-EL-0001 | overCurrentProtection | 过流保护 | Over Current Protection | 电流超过额定值 | 配电柜 | 7301 | {"level":"ERROR","outputParams":[{"dataType":"DOUBLE","key":"current","unit":{"unitCode":"ampere","unitSymbol":"A"}},{"dataType":"DOUBLE","key":"ratedCurrent","unit":{"unitCode":"ampere","unitSymbol":"A"}}]}
EVENT | E-EL-0002 | overVoltageProtection | 过压保护 | Over Voltage Protection | 电压超过上限 | 配电柜 | 7302 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"voltage","unit":{"unitCode":"volt","unitSymbol":"V"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"volt","unitSymbol":"V"}}]}
EVENT | E-EL-0003 | underVoltageProtection | 欠压保护 | Under Voltage Protection | 电压低于下限 | 配电柜 | 7303 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"voltage","unit":{"unitCode":"volt","unitSymbol":"V"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"volt","unitSymbol":"V"}}]}
EVENT | E-EL-0004 | transformerOverTemp | 变压器超温 | Transformer Over Temp | 变压器温度过高 | 变压器 | 7304 | {"level":"ERROR","outputParams":[{"dataType":"DOUBLE","key":"temperature","unit":{"unitCode":"celsius","unitSymbol":"℃"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"celsius","unitSymbol":"℃"}}]}
EVENT | E-EL-0005 | batteryLow | 电池电量低 | Battery Low | 电池剩余容量不足 | UPS/EPS | 7305 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"remaining","unit":{"unitCode":"percent","unitSymbol":"%"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"percent","unitSymbol":"%"}}]}
EVENT | E-EL-0006 | mainsPowerLoss | 市电中断 | Mains Power Loss | 市电供电中断 | UPS/EPS/发电机组 | 7306 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"duration","unit":{"unitCode":"second","unitSymbol":"s"}}]}
EVENT | E-EL-0007 | leakageAlarm | 漏电告警 | Leakage Alarm | 漏电电流超标 | 配电柜 | 7307 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"leakageCurrent","unit":{"unitCode":"milliampere","unitSymbol":"mA"}}]}
EVENT | E-FP-0001 | fireAlarm | 火灾报警 | Fire Alarm | 火灾探测器报警 | 火灾报警系统 | 7401 | {"level":"ERROR","outputParams":[{"dataType":"TEXT","key":"zone"},{"dataType":"ENUM","key":"detectorType"},{"dataType":"TEXT","key":"detectorId"}]}
EVENT | E-FP-0002 | pipeUnderPressure | 管网欠压 | Pipe Under Pressure | 消防管网压力不足 | 消防水系统 | 7402 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"pressure","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}},{"dataType":"DOUBLE","key":"limitValue","unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}]}
EVENT | E-FP-0003 | sprinklerActivated | 喷头动作 | Sprinkler Activated | 喷头破裂喷水 | 自动喷水系统 | 7403 | {"level":"ALERT","outputParams":[{"dataType":"TEXT","key":"zone"},{"dataType":"TEXT","key":"sprinklerId"}]}
EVENT | E-FP-0004 | gasDischarged | 气体喷放 | Gas Discharged | 气体灭火剂喷放 | 气体灭火系统 | 7404 | {"level":"ERROR","outputParams":[{"dataType":"TEXT","key":"zone"},{"dataType":"ENUM","key":"agentType"}]}
EVENT | E-FP-0005 | fireDoorNotClosed | 防火门未关闭 | Fire Door Not Closed | 防火门超时未关 | 防火门 | 7405 | {"level":"ALERT","outputParams":[{"dataType":"TEXT","key":"doorId"},{"dataType":"DOUBLE","key":"duration","unit":{"unitCode":"second","unitSymbol":"s"}}]}
EVENT | E-FP-0006 | detectorOffline | 探测器离线 | Detector Offline | 探测器通信中断 | 火灾报警系统 | 7406 | {"level":"ALERT","outputParams":[{"dataType":"TEXT","key":"detectorId"},{"dataType":"TEXT","key":"zone"}]}
EVENT | E-ELV-0001 | trappedPassenger | 困人事件 | Trapped Passenger | 电梯困人 | 电梯 | 7501 | {"level":"ERROR","outputParams":[{"dataType":"INT","key":"floor"},{"dataType":"TEXT","key":"carId"},{"dataType":"DOUBLE","key":"duration","unit":{"unitCode":"minute","unitSymbol":"min"}}]}
EVENT | E-ELV-0002 | overloadAlarm | 超载告警 | Overload Alarm | 轿厢超载 | 电梯 | 7502 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"currentLoad","unit":{"unitCode":"kilogram","unitSymbol":"kg"}},{"dataType":"INT","key":"ratedCapacity","unit":{"unitCode":"kilogram","unitSymbol":"kg"}}]}
EVENT | E-ELV-0003 | doorLockFault | 门锁故障 | Door Lock Fault | 层门/轿门锁故障 | 电梯 | 7503 | {"level":"ERROR","outputParams":[{"dataType":"INT","key":"floor"},{"dataType":"TEXT","key":"faultDesc"}]}
EVENT | E-ELV-0004 | speedGovernorTriggered | 限速器动作 | Speed Governor Triggered | 超速保护动作 | 电梯 | 7504 | {"level":"ERROR","outputParams":[{"dataType":"DOUBLE","key":"currentSpeed","unit":{"unitCode":"meter_per_second","unitSymbol":"m/s"}},{"dataType":"DOUBLE","key":"ratedSpeed","unit":{"unitCode":"meter_per_second","unitSymbol":"m/s"}}]}
EVENT | E-ELV-0005 | escalatorReverse | 扶梯逆行 | Escalator Reverse | 扶梯非预期反向运行 | 自动扶梯 | 7505 | {"level":"ERROR","outputParams":[{"dataType":"ENUM","key":"direction"}]}
EVENT | E-SM-0001 | illegalEntry | 非法闯入 | Illegal Entry | 未授权开门 | 门禁/入侵报警 | 7601 | {"level":"ALERT","outputParams":[{"dataType":"TEXT","key":"doorId"},{"dataType":"ENUM","key":"authMethod"},{"dataType":"DATE","key":"timestamp"}]}
EVENT | E-SM-0002 | doorOpenTimeout | 门超时未关 | Door Open Timeout | 门长时间未关闭 | 门禁 | 7602 | {"level":"ALERT","outputParams":[{"dataType":"TEXT","key":"doorId"},{"dataType":"DOUBLE","key":"duration","unit":{"unitCode":"second","unitSymbol":"s"}}]}
EVENT | E-SM-0003 | videoSignalLost | 视频信号丢失 | Video Signal Lost | 视频信号中断 | 摄像机 | 7603 | {"level":"ERROR","outputParams":[{"dataType":"TEXT","key":"cameraId"}]}
EVENT | E-SM-0004 | storageInsufficient | 存储空间不足 | Storage Insufficient | 存储即将满 | NVR/服务器 | 7604 | {"level":"ALERT","outputParams":[{"dataType":"DOUBLE","key":"usage","unit":{"unitCode":"percent","unitSymbol":"%"}},{"dataType":"DOUBLE","key":"remaining","unit":{"unitCode":"gigabyte","unitSymbol":"GB"}}]}
EVENT | E-SM-0005 | sensorValueAbnormal | 传感器数值异常 | Sensor Value Abnormal | 测量值超出正常范围 | 传感器 | 7605 | {"level":"ALERT","outputParams":[{"dataType":"TEXT","key":"parameterName"},{"dataType":"DOUBLE","key":"value"},{"dataType":"STRUCT","key":"normalRange"}]}
EVENT | E-SM-0006 | controllerOffline | 控制器离线 | Controller Offline | 控制器通信中断 | DDC/PLC | 7606 | {"level":"ALERT","outputParams":[{"dataType":"TEXT","key":"controllerId"},{"dataType":"DATE","key":"lastOnlineTime"}]}
SERVICE | S-HVAC-0001 | setTemperatureSvc | 设定温度 | Set Temperature | 设定目标温度 | 空调末端 | 8101 | {"callMode":"ASYNC","inputParams":[{"constraints":{"max":60,"min":-20},"dataType":"DOUBLE","key":"temperature","unit":{"unitCode":"celsius","unitSymbol":"℃"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-HVAC-0002 | setOperationMode | 切换运行模式 | Set Operation Mode | 切换制冷/制热 | 冷机/热泵/空调末端 | 8102 | {"callMode":"ASYNC","inputParams":[{"dataType":"ENUM","key":"mode"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-HVAC-0003 | setDamperPosition | 设定风阀开度 | Set Damper Position | 调节风阀开度 | 通风机/空调末端 | 8103 | {"callMode":"ASYNC","inputParams":[{"constraints":{"max":100,"min":0},"dataType":"DOUBLE","key":"position","unit":{"unitCode":"percent","unitSymbol":"%"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-HVAC-0004 | setValvePosition | 设定水阀开度 | Set Valve Position | 调节水阀开度 | 空调末端/换热器 | 8104 | {"callMode":"ASYNC","inputParams":[{"constraints":{"max":100,"min":0},"dataType":"DOUBLE","key":"position","unit":{"unitCode":"percent","unitSymbol":"%"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-HVAC-0005 | setFanFrequency | 设定风机频率 | Set Fan Frequency | 调节变频器频率 | 通风机/变频空调 | 8105 | {"callMode":"ASYNC","inputParams":[{"constraints":{"max":100,"min":0},"dataType":"DOUBLE","key":"frequency","unit":{"unitCode":"hertz","unitSymbol":"Hz"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-HVAC-0006 | setFanSpeedSvc | 设定风速 | Set Fan Speed | 设定风机档位 | 空调末端 | 8106 | {"callMode":"ASYNC","inputParams":[{"dataType":"ENUM","key":"speed"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-WP-0001 | setPumpFrequency | 设定水泵频率 | Set Pump Frequency | 调节水泵变频器频率 | 变频水泵 | 8201 | {"callMode":"ASYNC","inputParams":[{"constraints":{"max":100,"min":0},"dataType":"DOUBLE","key":"frequency","unit":{"unitCode":"hertz","unitSymbol":"Hz"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-WP-0002 | setWaterTempSvc | 设定水温 | Set Water Temp | 设定目标热水温度 | 热水设备 | 8202 | {"callMode":"ASYNC","inputParams":[{"constraints":{"max":80,"min":20},"dataType":"DOUBLE","key":"temperature","unit":{"unitCode":"celsius","unitSymbol":"℃"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-WP-0003 | switchStandbyPump | 切换备用泵 | Switch Standby Pump | 切换至指定备用泵 | 水泵组 | 8203 | {"callMode":"ASYNC","inputParams":[{"dataType":"INT","key":"pumpIndex"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-EL-0001 | closeSwitch | 合闸 | Close Switch | 合上指定回路开关 | 配电柜/箱 | 8301 | {"callMode":"ASYNC","inputParams":[{"dataType":"INT","key":"circuitIndex"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-EL-0002 | openSwitch | 分闸 | Open Switch | 断开指定回路开关 | 配电柜/箱 | 8302 | {"callMode":"ASYNC","inputParams":[{"dataType":"INT","key":"circuitIndex"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-EL-0003 | setDimmingLevel | 设定调光级别 | Set Dimming Level | 调节照明亮度 | 照明设备 | 8303 | {"callMode":"ASYNC","inputParams":[{"constraints":{"max":100,"min":0},"dataType":"DOUBLE","key":"level","unit":{"unitCode":"percent","unitSymbol":"%"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-EL-0004 | setLightingScene | 切换照明场景 | Set Lighting Scene | 切换预设照明场景 | 照明设备 | 8304 | {"callMode":"ASYNC","inputParams":[{"dataType":"TEXT","key":"sceneId"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-FP-0001 | startFirePump | 启动消防泵 | Start Fire Pump | 远程启动消防水泵 | 消防水泵 | 8401 | {"callMode":"ASYNC","inputParams":[{"dataType":"INT","key":"pumpIndex"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-FP-0002 | systemSelfTest | 系统自检 | System Self Test | 触发系统自检 | 火灾报警系统 | 8402 | {"callMode":"ASYNC","outputParams":[{"dataType":"STRUCT","key":"result"}]}
SERVICE | S-FP-0003 | silenceAlarm | 消音 | Silence Alarm | 消除报警声响 | 火灾报警系统 | 8403 | {"callMode":"ASYNC","outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-FP-0004 | resetSystem | 复位 | Reset System | 系统复位 | 火灾报警系统 | 8404 | {"callMode":"ASYNC","outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-ELV-0001 | callElevator | 呼梯 | Call Elevator | 外呼电梯 | 电梯 | 8501 | {"callMode":"ASYNC","inputParams":[{"dataType":"INT","key":"floor"},{"dataType":"ENUM","key":"direction"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-ELV-0002 | lockElevator | 锁梯 | Lock Elevator | 锁定/解锁电梯 | 电梯 | 8502 | {"callMode":"ASYNC","inputParams":[{"dataType":"BOOL","key":"lock"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-ELV-0003 | fireReturn | 消防返回 | Fire Return | 触发消防迫降 | 电梯 | 8503 | {"callMode":"ASYNC","outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-ELV-0004 | setEscalatorDirection | 切换扶梯方向 | Set Escalator Direction | 切换扶梯运行方向 | 自动扶梯 | 8504 | {"callMode":"ASYNC","inputParams":[{"dataType":"ENUM","key":"direction"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-SM-0001 | remoteOpenDoor | 远程开门 | Remote Open Door | 远程开启指定门 | 门禁 | 8601 | {"callMode":"ASYNC","inputParams":[{"dataType":"TEXT","key":"doorId"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-SM-0002 | armSystem | 布防 | Arm System | 设定布防模式 | 入侵报警 | 8602 | {"callMode":"ASYNC","inputParams":[{"dataType":"ENUM","key":"armMode"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-SM-0003 | ptzControl | 云台控制 | PTZ Control | 控制云台方向和速度 | 摄像机 | 8603 | {"callMode":"ASYNC","inputParams":[{"dataType":"ENUM","key":"action"},{"constraints":{"max":10,"min":1},"dataType":"INT","key":"speed"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-SM-0004 | setControlOutput | 设定控制输出 | Set Control Output | 设定模拟输出值 | 控制器 | 8604 | {"callMode":"ASYNC","inputParams":[{"dataType":"INT","key":"outputIndex"},{"constraints":{"max":100,"min":0},"dataType":"DOUBLE","key":"value"}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
SERVICE | S-SM-0005 | publishMessage | 发布信息 | Publish Message | 发布显示内容 | 信息发布 | 8605 | {"callMode":"ASYNC","inputParams":[{"dataType":"TEXT","key":"content"},{"dataType":"INT","key":"duration","unit":{"unitCode":"second","unitSymbol":"s"}}],"outputParams":[{"dataType":"BOOL","key":"success"}]}
RELATION | R-HVAC-0001 | copDerivedFrom | 实时COP派生关系 | COP Derived From | 实时COP由实时制冷量与功率派生 (currentCOP = currentCoolingCapacity / currentPower) | 制冷机组 | 9101 | {"cardinality":"oneToOne","directional":true,"relationType":"derivedFrom","source":{"identifier":"currentCOP","kind":"feature"},"target":{"identifier":"currentCoolingCapacity","kind":"feature"}}
RELATION | R-HVAC-0002 | supplyReturnTempPair | 供回水温度关系 | Supply-Return Temp Pair | 供水温度与回水温度的关联，用于温差计算 | 冷机/锅炉/换热器 | 9102 | {"cardinality":"oneToOne","directional":false,"relationType":"relatedTo","source":{"identifier":"supplyWaterTemp","kind":"feature"},"target":{"identifier":"returnWaterTemp","kind":"feature"}}
RELATION | R-HVAC-0003 | compressorStatusDependsOnPower | 压缩机状态依赖开关 | Compressor Depends On Power | 压缩机运行状态依赖于设备开关 | 制冷机组 | 9103 | {"cardinality":"manyToOne","directional":true,"relationType":"dependsOn","source":{"identifier":"compressorStatus","kind":"feature"},"target":{"identifier":"powerSwitch","kind":"feature"}}
RELATION | R-EL-0001 | loadRateFromActivePower | 负载率派生关系 | Load Rate Derived | 变压器负载率由有功功率/额定功率派生 | 变压器 | 9301 | {"cardinality":"oneToOne","directional":true,"relationType":"derivedFrom","source":{"identifier":"loadRate","kind":"feature"},"target":{"identifier":"activePower","kind":"feature"}}
RELATION | R-FP-0001 | fireAlarmTriggersDoorRelease | 火警触发防火门释放 | Fire Alarm Triggers Door Release | 火灾报警时触发防火门释放（控制链） | 消防系统 | 9401 | {"cardinality":"oneToMany","directional":true,"relationType":"controls","source":{"identifier":"alarmStatus","kind":"feature"},"target":{"identifier":"fireDoorStatus","kind":"feature"}}
RELATION | R-ELV-0001 | fireReturnControlsLockStatus | 消防返回控制锁梯 | Fire Return Controls Lock | 消防返回触发时电梯进入锁梯状态 | 电梯 | 9501 | {"cardinality":"oneToOne","directional":true,"relationType":"controls","source":{"identifier":"fireReturnStatus","kind":"feature"},"target":{"identifier":"lockStatus","kind":"feature"}}
PROPERTY | RAT-HVAC-CH-001 | ratedCoolingCapacity | 额定制冷量 | Rated Cooling Capacity | 铭牌额定制冷量 | 制冷机组 | 51101 | {"accessMode":"R","category":"rated","constraints":{"max":50000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | RAT-HVAC-CH-002 | ratedHeatingCapacity | 额定制热量 | Rated Heating Capacity | 热泵机组适用 | 制冷机组 | 51102 | {"accessMode":"R","category":"rated","constraints":{"max":50000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | RAT-HVAC-CH-003 | ratedInputPower | 额定输入功率 | Rated Input Power | 额定工况输入功率 | 制冷机组 | 51103 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | RAT-HVAC-CH-004 | ratedCOP | 额定COP | Rated COP | 额定性能系数 | 制冷机组 | 51104 | {"accessMode":"R","category":"rated","constraints":{"max":15,"min":0},"dataType":"DOUBLE","isRated":true}
PROPERTY | RAT-HVAC-CH-005 | ratedEER | 额定EER | Rated EER | 额定能效比 | 制冷机组 | 51105 | {"accessMode":"R","category":"rated","constraints":{"max":15,"min":0},"dataType":"DOUBLE","isRated":true}
PROPERTY | RAT-HVAC-CH-006 | ratedIPLV | 额定IPLV | Rated IPLV | 综合部分负荷性能系数 | 制冷机组 | 51106 | {"accessMode":"R","category":"rated","constraints":{"max":15,"min":0},"dataType":"DOUBLE","isRated":true}
PROPERTY | RAT-HVAC-CH-007 | refrigerantType | 制冷剂类型 | Refrigerant Type | 制冷剂种类 | 制冷机组 | 51107 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"R410A","value":0},{"label":"R134a","value":1},{"label":"R32","value":2},{"label":"R407C","value":3},{"label":"R290","value":4},{"label":"R717","value":5},{"label":"其他","value":6}],"isRated":true}
PROPERTY | RAT-HVAC-CH-008 | refrigerantCharge | 制冷剂充注量 | Refrigerant Charge | 制冷剂充注质量 | 制冷机组 | 51108 | {"accessMode":"R","category":"rated","constraints":{"max":5000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilogram","unitSymbol":"kg"}}
PROPERTY | RAT-HVAC-CH-009 | ratedChilledWaterFlow | 冷冻水额定流量 | Rated Chilled Water Flow | 额定冷冻水流量 | 制冷机组 | 51109 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | RAT-HVAC-CH-010 | ratedCondenserWaterFlow | 冷却水额定流量 | Rated Condenser Water Flow | 额定冷却水流量 | 制冷机组 | 51110 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | RAT-HVAC-CH-011 | ratedChilledWaterTemp | 冷冻水进出水温度 | Rated Chilled Water Temp | 额定冷冻水供回水温度 | 制冷机组 | 51111 | {"accessMode":"R","category":"rated","dataType":"STRUCT","isRated":true,"structFields":[{"constraints":{"max":40,"min":0},"dataType":"DOUBLE","key":"inlet","unit":{"unitCode":"celsius","unitSymbol":"℃"}},{"constraints":{"max":40,"min":0},"dataType":"DOUBLE","key":"outlet","unit":{"unitCode":"celsius","unitSymbol":"℃"}}]}
PROPERTY | RAT-HVAC-CH-012 | ratedCondenserWaterTemp | 冷却水进出水温度 | Rated Condenser Water Temp | 额定冷却水进出水温度 | 制冷机组 | 51112 | {"accessMode":"R","category":"rated","dataType":"STRUCT","isRated":true,"structFields":[{"constraints":{"max":50,"min":0},"dataType":"DOUBLE","key":"inlet","unit":{"unitCode":"celsius","unitSymbol":"℃"}},{"constraints":{"max":50,"min":0},"dataType":"DOUBLE","key":"outlet","unit":{"unitCode":"celsius","unitSymbol":"℃"}}]}
PROPERTY | RAT-HVAC-CH-013 | compressorType | 压缩机类型 | Compressor Type | 压缩机形式 | 制冷机组 | 51113 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"离心式","value":0},{"label":"螺杆式","value":1},{"label":"涡旋式","value":2},{"label":"活塞式","value":3},{"label":"转子式","value":4}],"isRated":true}
PROPERTY | RAT-HVAC-CH-014 | compressorCount | 压缩机数量 | Compressor Count | 压缩机台数 | 制冷机组 | 51114 | {"accessMode":"R","category":"rated","constraints":{"max":20,"min":1},"dataType":"INT","isRated":true}
PROPERTY | RAT-HVAC-CH-015 | ratedWaterResistance | 额定水阻力 | Rated Water Resistance | 额定水侧压降 | 制冷机组 | 51115 | {"accessMode":"R","category":"rated","constraints":{"max":1000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kpa","unitSymbol":"kPa"}}
PROPERTY | RAT-HVAC-BL-001 | ratedThermalPower | 额定热功率 | Rated Thermal Power | 额定热输出功率 | 锅炉 | 51201 | {"accessMode":"R","category":"rated","constraints":{"max":100,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"megawatt","unitSymbol":"MW"}}
PROPERTY | RAT-HVAC-BL-002 | ratedWorkingPressure | 额定工作压力 | Rated Working Pressure | 额定蒸汽/热水压力 | 锅炉 | 51202 | {"accessMode":"R","category":"rated","constraints":{"max":10,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}
PROPERTY | RAT-HVAC-BL-003 | ratedSupplyTemp | 额定供水温度 | Rated Supply Temp | 额定出口水温 | 锅炉 | 51203 | {"accessMode":"R","category":"rated","constraints":{"max":250,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | RAT-HVAC-BL-004 | ratedReturnTemp | 额定回水温度 | Rated Return Temp | 额定回水温度 | 锅炉 | 51204 | {"accessMode":"R","category":"rated","constraints":{"max":200,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | RAT-HVAC-BL-005 | ratedEfficiency | 额定热效率 | Rated Efficiency | 额定热效率 | 锅炉 | 51205 | {"accessMode":"R","category":"rated","constraints":{"max":100,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | RAT-HVAC-BL-006 | fuelType | 燃料类型 | Fuel Type | 燃料种类 | 锅炉 | 51206 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"天然气","value":0},{"label":"柴油","value":1},{"label":"电","value":2},{"label":"生物质","value":3},{"label":"液化石油气","value":4},{"label":"煤","value":5}],"isRated":true}
PROPERTY | RAT-HVAC-BL-007 | ratedFuelConsumption | 额定燃料耗量 | Rated Fuel Consumption | 额定工况燃料消耗 | 锅炉 | 51207 | {"accessMode":"R","category":"rated","dataType":"DOUBLE","isRated":true}
PROPERTY | RAT-HVAC-BL-008 | ratedWaterVolume | 额定水容量 | Rated Water Volume | 锅炉容水量 | 锅炉 | 51208 | {"accessMode":"R","category":"rated","constraints":{"max":100,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter","unitSymbol":"m³"}}
PROPERTY | RAT-HVAC-HX-001 | ratedHeatTransfer | 额定换热量 | Rated Heat Transfer | 额定换热能力 | 换热器 | 51301 | {"accessMode":"R","category":"rated","constraints":{"max":50000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | RAT-HVAC-HX-002 | heatExchangerType | 换热器类型 | Heat Exchanger Type | 换热器形式 | 换热器 | 51302 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"板式","value":0},{"label":"壳管式","value":1},{"label":"容积式","value":2},{"label":"翅片式","value":3}],"isRated":true}
PROPERTY | RAT-HVAC-HX-003 | ratedPrimaryFlow | 一次侧额定流量 | Rated Primary Flow | 一次侧额定流量 | 换热器 | 51303 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | RAT-HVAC-HX-004 | ratedSecondaryFlow | 二次侧额定流量 | Rated Secondary Flow | 二次侧额定流量 | 换热器 | 51304 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | RAT-HVAC-HX-007 | hxRatedWorkingPressure | 额定工作压力 | Rated Working Pressure (HX) | 额定承压 | 换热器 | 51307 | {"accessMode":"R","category":"rated","constraints":{"max":10,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"megapascal","unitSymbol":"MPa"}}
PROPERTY | RAT-HVAC-TU-001 | tuRatedCoolingCapacity | 空调末端额定制冷量 | TU Rated Cooling Capacity | 末端额定制冷量 | 空调末端 | 51401 | {"accessMode":"R","category":"rated","constraints":{"max":500,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | RAT-HVAC-TU-002 | tuRatedHeatingCapacity | 空调末端额定制热量 | TU Rated Heating Capacity | 末端额定制热量 | 空调末端 | 51402 | {"accessMode":"R","category":"rated","constraints":{"max":500,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}
PROPERTY | RAT-HVAC-TU-003 | ratedAirVolume | 额定风量 | Rated Air Volume | 额定风量 | 空调末端 | 51403 | {"accessMode":"R","category":"rated","constraints":{"max":100000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | RAT-HVAC-TU-004 | ratedExternalPressure | 额定余压 | Rated External Pressure | 额定机外余压 | 空调末端 | 51404 | {"accessMode":"R","category":"rated","constraints":{"max":2000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"pascal","unitSymbol":"Pa"}}
PROPERTY | RAT-HVAC-FN-001 | fnRatedAirVolume | 通风机额定风量 | Fan Rated Air Volume | 额定工况风量 | 通风机 | 51501 | {"accessMode":"R","category":"rated","constraints":{"max":500000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | RAT-HVAC-FN-002 | ratedTotalPressure | 额定全压 | Rated Total Pressure | 额定全压 | 通风机 | 51502 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"pascal","unitSymbol":"Pa"}}
PROPERTY | RAT-HVAC-FN-003 | ratedStaticPressure | 额定静压 | Rated Static Pressure | 额定静压 | 通风机 | 51503 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"pascal","unitSymbol":"Pa"}}
PROPERTY | RAT-HVAC-FN-004 | fanType | 风机类型 | Fan Type | 风机形式 | 通风机 | 51504 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"离心式","value":0},{"label":"轴流式","value":1},{"label":"混流式","value":2},{"label":"斜流式","value":3},{"label":"屋顶式","value":4}],"isRated":true}
PROPERTY | RAT-HVAC-CT-001 | ctRatedWaterFlow | 冷却塔额定水量 | CT Rated Water Flow | 额定冷却水量 | 冷却塔 | 51601 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | RAT-HVAC-CT-002 | ctRatedInletTemp | 冷却塔额定进水温度 | CT Rated Inlet Temp | 额定进水温度 | 冷却塔 | 51602 | {"accessMode":"R","category":"rated","constraints":{"max":60,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | RAT-HVAC-CT-003 | ctRatedOutletTemp | 冷却塔额定出水温度 | CT Rated Outlet Temp | 额定出水温度 | 冷却塔 | 51603 | {"accessMode":"R","category":"rated","constraints":{"max":50,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | RAT-HVAC-CT-004 | ratedWetBulbTemp | 额定湿球温度 | Rated Wet Bulb Temp | 设计湿球温度 | 冷却塔 | 51604 | {"accessMode":"R","category":"rated","constraints":{"max":40,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"celsius","unitSymbol":"℃"}}
PROPERTY | RAT-WP-PM-001 | ratedFlowRate | 额定流量 | Rated Flow Rate | 额定工况流量 | 水泵 | 52101 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"cubic_meter_per_hour","unitSymbol":"m³/h"}}
PROPERTY | RAT-WP-PM-002 | ratedHead | 额定扬程 | Rated Head | 额定扬程 | 水泵 | 52102 | {"accessMode":"R","category":"rated","constraints":{"max":500,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"meter","unitSymbol":"m"}}
PROPERTY | RAT-WP-PM-003 | pumpType | 水泵类型 | Pump Type | 水泵形式 | 水泵 | 52103 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"离心式","value":0},{"label":"轴流式","value":1},{"label":"混流式","value":2},{"label":"潜水式","value":3},{"label":"管道式","value":4},{"label":"隔膜式","value":5}],"isRated":true}
PROPERTY | RAT-EL-TR-001 | ratedCapacity | 额定容量 | Rated Capacity | 额定视在功率 | 变压器 | 53101 | {"accessMode":"R","category":"rated","constraints":{"max":100000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kva","unitSymbol":"kVA"}}
PROPERTY | RAT-EL-TR-002 | ratedPrimaryVoltage | 一次侧额定电压 | Rated Primary Voltage | 高压侧额定电压 | 变压器 | 53102 | {"accessMode":"R","category":"rated","constraints":{"max":500,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilovolt","unitSymbol":"kV"}}
PROPERTY | RAT-EL-TR-003 | ratedSecondaryVoltage | 二次侧额定电压 | Rated Secondary Voltage | 低压侧额定电压 | 变压器 | 53103 | {"accessMode":"R","category":"rated","constraints":{"max":100,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilovolt","unitSymbol":"kV"}}
PROPERTY | RAT-ELV-EL-001 | elvRatedCapacity | 电梯额定载重量 | Elevator Rated Capacity | 额定载重 | 电梯 | 55101 | {"accessMode":"R","category":"rated","constraints":{"max":20000,"min":0},"dataType":"INT","isRated":true,"unit":{"unitCode":"kilogram","unitSymbol":"kg"}}
PROPERTY | RAT-ELV-EL-002 | ratedSpeed | 电梯额定速度 | Elevator Rated Speed | 额定运行速度 | 电梯 | 55102 | {"accessMode":"R","category":"rated","constraints":{"max":20,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"meter_per_second","unitSymbol":"m/s"}}
PROPERTY | RAT-ELV-EL-003 | floorCount | 层站数 | Floor Count | 服务楼层总数 | 电梯 | 55103 | {"accessMode":"R","category":"rated","constraints":{"max":200,"min":1},"dataType":"INT","isRated":true}
PROPERTY | RAT-ELV-EL-004 | liftHeight | 提升高度 | Lift Height | 总垂直行程 | 电梯 | 55104 | {"accessMode":"R","category":"rated","constraints":{"max":600,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"meter","unitSymbol":"m"}}
PROPERTY | RAT-ELV-EL-005 | elevatorType | 电梯类型 | Elevator Type | 电梯用途分类 | 电梯 | 55105 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"乘客","value":0},{"label":"载货","value":1},{"label":"医用","value":2},{"label":"汽车","value":3},{"label":"消防","value":4},{"label":"观光","value":5},{"label":"防爆","value":6}],"isRated":true}
PROPERTY | RAT-SM-CM-001 | resolution | 分辨率 | Resolution | 视频分辨率 | 摄像机 | 56101 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"720P","value":0},{"label":"1080P","value":1},{"label":"2K","value":2},{"label":"4K","value":3},{"label":"8K","value":4}],"isRated":true}
PROPERTY | RAT-SM-CM-002 | sensorType | 传感器类型 | Sensor Type | 图像传感器类型 | 摄像机 | 56102 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"CMOS","value":0},{"label":"CCD","value":1}],"isRated":true}
PROPERTY | RAT-AX-PV-001 | ratedPeakPower | 额定峰值功率 | Rated Peak Power | 额定峰值功率 | 光伏 | 57101 | {"accessMode":"R","category":"rated","constraints":{"max":10000,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kwp","unitSymbol":"kWp"}}
PROPERTY | RAT-AX-PV-002 | moduleEfficiency | 组件转换效率 | Module Efficiency | 光伏组件转换效率 | 光伏 | 57102 | {"accessMode":"R","category":"rated","constraints":{"max":50,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"percent","unitSymbol":"%"}}
PROPERTY | RAT-AX-CP-001 | chargingType | 充电类型 | Charging Type | 充电模式 | 充电桩 | 57201 | {"accessMode":"R","category":"rated","dataType":"ENUM","enumItems":[{"label":"交流慢充","value":0},{"label":"直流快充","value":1}],"isRated":true}
PROPERTY | RAT-AX-CP-002 | cpRatedPower | 充电桩额定功率 | CP Rated Power | 额定充电功率 | 充电桩 | 57202 | {"accessMode":"R","category":"rated","constraints":{"max":500,"min":0},"dataType":"DOUBLE","isRated":true,"unit":{"unitCode":"kilowatt","unitSymbol":"kW"}}